The Diffusion Highwall 200

Fan coil unit

General

Designed for specific applications where a vertical wall mounted unit with the ability to accept up to 50Pa external static pressure is a requirement together with extremely quiet operation. Typical applications include hotel and hospital bedrooms and installations where a discreet wall or furniture recessed fan coil unit is a pre-requisite.

# Highwall 200 series Waterside Control

| Size | Speed | Air Volume | Cooling Performance |  | Water |  | Heating Capacity | Water |  | Guide Noise |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | l/s | Total kW | Sensible kW | Flow kg/s | P.D kPa | kW | Flow kg/s | P.D kPa | NR* |
| 1 | Low | 110 | 2.11 | 1.65 | 0.1 | 7.5 | 1.04 | 0.03 | 0.9 | 30 |
| 1 | Med. | 130 | 2.38 | 1.88 | 0.1 | 7.5 | 1.2 | 0.03 | 0.9 | 35 |
| 1 | High | 170 | 2.83 | 2.43 | 0.1 | 7.5 | 1.5 | 0.03 | 0.9 | 40 |
| 2 | Low | 170 | 3.46 | 2.63 | 0.17 | 21.1 | 1.6 | 0.04 | 1.8 | 30 |
| 2 | Med. | 200 | 3.88 | 3.0 | 0.17 | 21.1 | 1.8 | 0.04 | 1.8 | 35 |
| 2 | High | 250 | 4.48 | 3.54 | 0.17 | 21.1 | 2.05 | 0.04 | 1.8 | 40 |
| 3 | Low | 210 | 4.3 | 3.27 | 0.22 | 20.2 | 2.1 | 0.05 | 3.3 | 30 |
| 3 | Med. | 260 | 5.08 | 3.91 | 0.22 | 20.2 | 2.4 | 0.05 | 3.3 | 35 |
| 3 | High | 310 | 5.64 | 4.46 | 0.22 | 20.2 | 2.62 | 0.05 | 3.3 | 40 |

Cooling based upon return air at 22oCdb and 15.6 oCwb. Heating based upon return air at 21oC.  Flow rates based upon chilled water 5.5 / 11oC.  Low Pressure Hot water 82/71oC . Water flow set for medium speed.

* NR levels are given for guidance only. Full Sound Power Spectra are available on request and should be used to calculate the actual level specific to a given room.

Diffusion Environmental systems have a policy of continuous product development and therefore reserve the right to change information given within this data sheet without prior notice.